## Sheet1
|  |  | CI66 |  |  |  |  | Nordic |  |  |  |  | EcoNordic
| pyflexit Register Name | Description | Modbus address | Register Type | Data Type | Unit | Range | Modbus address | Register Type | Data Type | Unit | Range | Modbus address | Register Type | Data Type | Unit | Range
Temperatures | SetpointAwaySupplyAirTemp | Temperature setpoint in Away mode | [5 empty] | 1163 | Holding | f | °C |  | 1163 | Holding | f | °C
| SetpointHomeSupplyAirTemp | Temperature setpoint in Home mode | [5 empty] | 1155 | Holding | f | °C |  | 1155 | Holding | f | °C
| SetpointSupplyAirTemp | Setpoint temperature | 9 | Holding | h | 0.1 °C
| OutsideAirTemp | Outside air temperature | 12 | Input | h | 0.1 °C |  | 1 | Input | f | °C |  | 1 | Input | f | °C
| SupplyAirTemp | Supply air temperature | 10 | Input | h | 0.1 °C |  | 5 | Input | f | °C |  | 5 | Input | f | °C
| ExtractAirTemp | Extract air temperature | 11 | Input | h | 0.1 °C |  | 9 | Input | f | °C |  | 9 | Input | f | °C
| ExhaustAirTemp | Exhaust air temperature | [5 empty] | 13 | Input | f | °C |  | 13 | Input | f | °C
Fan mode | VentMode | Present Ventilation mode | 17 | Input | h |  | ?? | 3034 | Input | H |  | [ 1 : Off ¦ 2 : Away ¦ 3 : Home ¦ 4 : High ¦ 5 : Fume hood ¦ 6 : Fireplace ¦ 7 : Temporary high] ¦ ] | 3034 | Input | H |  | [ 1 : Off ¦ 2 : Away ¦ 3 : Home ¦ 4 : High ¦ 5 : Fume hood ¦ 6 : Fireplace ¦ 7 : Temporary high] ¦ ]
| SetVentMode | Select Ventilation mode | 18 | Holding | h |  | ?? | 2013 | Holding | H |  | [ 1 : Stop ¦ 2 : Away ¦ 3 : Home ¦ 4 : High] ¦ ] | 2013 | Holding | H |  | [ 1 : Stop ¦ 2 : Away ¦ 3 : Home ¦ 4 : High] ¦ ]
Heating | HeatExchangerSpeed | Rotary heat exchanger speed | 15 | Input | h | % |  | 1 | Holding | f | % |  | 1 | Holding | f | %
| ElectricHeaterPowerSupplyAir | Electrical supply air heater | 16 | Input | h | % |  | 13 | Holding | f | % |  | 13 | Holding | f | %
Filter | FilterRunTime | Running hours since last filter change | 9 | Input | H | h |  | 1271 | Holding | f | h |  | 1271 | Holding | f | h
| FilterRemainingTime | Time until next filter change | [5 empty] | 1269 | Holding | f | h |  | 1269 | Holding | f | h